## Open Snags
05 Open snag list: Qamar Bay
Halcyon handover folder, 1 October 2031. Items open at handover.
Synthetic: for training only. Deep Hospitality.
Ref | Location | Description | Category | Life safety | Priority | Date raised | Status | Responsible (per Halcyon)
SN-001 | Spa extension, treatment rooms 7 and 8 | Fire alarm sounder not audible inside treatment rooms with doors closed (measured 58 dB) | Fire and life safety | Yes | High | 12 July 2031 | Open | Owner's contractor
SN-002 | Spa corridor | Fire door closer failed; door does not self-close and latch | Fire and life safety | Yes | High | 14 June 2031 | Open | Hotel engineering
SN-003 | Kids' club, rear exit | Emergency lighting fitting failed on 3-hour duration test | Fire and life safety | Yes | High | 19 June 2031 | Open | Supplier under warranty
SN-004 | Back of house, dry store B | Sprinkler heads obstructed by shelving stacked within 450 mm | Fire and life safety | Yes | High | 20 June 2031 | Open | Hotel engineering
SN-005 | Family pool | Lifebuoy and reaching pole missing from rescue station 2 | Fire and life safety | Yes | High | 3 June 2031 | Open | Specialist contractor
SN-006 | Kitchen, main line | Kitchen hood fire suppression system service overdue (last service March 2031) | Fire and life safety | Yes | High | 15 June 2031 | Open | Hotel engineering
SN-007 | Guestroom 214 | Balcony door seal failing; sand ingress | Building fabric | No | Medium | 4 September 2031 | Open | Hotel engineering
SN-008 | Guestroom 118 | Balcony door seal failing; noise from kids' club audible | Building fabric | No | Medium | 20 June 2031 | Open | Hotel engineering
SN-009 | Guestroom 305 | Bathroom silicone discoloured | Finishes | No | Low | 22 June 2031 | Open | Specialist contractor
SN-010 | Guestrooms 220 to 226 | Corridor carpet worn at lift lobby threshold | Finishes | No | Low | 3 July 2031 | Open | Hotel engineering
SN-011 | Suite 410 | Shower mixer temperature unstable | MEP | No | Medium | 19 July 2031 | Open | Supplier under warranty
SN-012 | Lobby | Two downlights failed above reception desk | MEP | No | Low | 15 July 2031 | Open | Hotel engineering
SN-013 | Lobby lounge | Coffee machine water filter housing leaking | Equipment | No | Medium | 20 August 2031 | Open | Hotel engineering
SN-014 | All-day dining | Terrace awning motor intermittent | Equipment | No | Low | 5 July 2031 | Open | Supplier under warranty
SN-015 | Beach grill | Extract fan bearing noise | MEP | No | Medium | 5 June 2031 | Open | Hotel engineering
SN-016 | Main pool deck | Three deck tiles cracked near the pool-side juice kiosk | Finishes | No | Medium | 21 July 2031 | Open | Specialist contractor
SN-017 | Spa relaxation lounge | Ceiling access panel misaligned | Finishes | No | Low | 23 September 2031 | Open | Supplier under warranty
SN-018 | Spa steam room | Steam generator fault code E4 recurring | Equipment | No | Medium | 16 September 2031 | Open | Supplier under warranty
SN-019 | Fitness centre | Treadmill 3 belt slipping | Equipment | No | Low | 11 July 2031 | Open | Hotel engineering
SN-020 | Kids' club | Soft play netting torn at upper level | Equipment | No | Medium | 24 July 2031 | Open | Hotel engineering
SN-021 | Meeting room | Projector screen motor faulty | Equipment | No | Low | 20 August 2031 | Open | Specialist contractor
SN-022 | Back of house corridor | Wall protection rail detached at loading bay | Finishes | No | Low | 12 September 2031 | Open | Supplier under warranty
SN-023 | Staff canteen | Hot holding unit thermostat inaccurate | Equipment | No | Medium | 21 June 2031 | Open | Hotel engineering
SN-024 | Laundry chute, level 3 | Chute door not closing fully | Building fabric | No | Medium | 18 September 2031 | Open | Hotel engineering
SN-025 | Plant room, chiller 2 | Chiller 2 compressor high head pressure alarms (see capex file 06) | MEP | No | High | 26 August 2031 | Open | Hotel engineering
SN-026 | Car park | Line markings faded at drop-off | External | No | Low | 17 September 2031 | Open | Hotel engineering
SN-027 | Beach pavilion 3 | Shade fabric torn | External | No | Low | 23 June 2031 | Open | Supplier under warranty
SN-028 | Guestroom 127 | Television mounting bracket loose | Equipment | No | Low | 12 August 2031 | Open | Specialist contractor
SN-029 | Guestroom 131 | Wardrobe door hinge broken | Finishes | No | Low | 20 September 2031 | Open | Hotel engineering
SN-030 | Suite 402 | Bathtub drain slow | MEP | No | Low | 4 August 2031 | Open | Specialist contractor
SN-031 | Guestroom 240 | Air conditioning fan coil noisy at high speed | MEP | No | Medium | 24 June 2031 | Open | Hotel engineering
SN-032 | Guestroom 112 | Connecting door lock misaligned | Building fabric | No | Medium | 25 August 2031 | Open | Specialist contractor
SN-033 | Main kitchen | Walk-in chiller door gasket damaged | Equipment | No | Medium | 11 September 2031 | Open | Supplier under warranty
SN-034 | Pastry kitchen | Blast chiller alarm faulty | Equipment | No | Medium | 2 September 2031 | Open | Supplier under warranty
SN-035 | Spa reception | Retail display lighting failed | MEP | No | Low | 7 June 2031 | Open | Specialist contractor
SN-036 | Roof | Two roof drain grates missing | Building fabric | No | Medium | 3 July 2031 | Open | Supplier under warranty
SN-037 | External boundary | Beach access gate latch broken | External | No | Low | 6 July 2031 | Open | Specialist contractor
| Open items | 37
| Of which life safety | 6